## Read me
BPEX | Building Performance Explained
Part L 2026 constructions for IES VE
Key information for reports ¦ BPEX construction scripts
WHAT THIS IS
Purpose | A summary of the constructions created by the BPEX Part L 2026 scripts for IES VE: what each one is for, its U-value, its thermal mass and where the values come from - the information you need to describe them in a report.
Scripts | BPEX_PartL_2026_Dwellings.py (19 constructions) ¦ BPEX_PartL_2026_NonDomestic.py (15 constructions)
NAMES IN IES VE
Pattern | Part L 2026_<DWL or NDOM>_<element> <use>_<U-value> e.g. Part L 2026_DWL_External Wall Extension_0.18
Standard | One value applies to both new and existing elements.
New | New buildings only.
Extension | Extensions, and new or replacement elements in existing buildings (dwellings only - non-domestic uses Standard).
Existing Improved | An existing element being upgraded: the "improved" U-value it should reach.
Existing Threshold | An existing element at the "threshold" U-value - the worst it can be before an upgrade is required.
POINTS FOR YOUR WRITE-UP
Limiting values | These are maximum (limiting) U-values. New buildings must also meet whole-building energy targets, which usually need better fabric (AD L Vol 1, note to Table 3.1).
U-value | Calculated to BS EN ISO 6946, the same method IES VE uses. IES VE reproduces these values.
Thermal mass (κ) | Areal heat capacity in kJ/m²K, BS EN ISO 13786 simplified method as used by IES VE.
Ground floors | Include an equivalent ground layer (BS EN ISO 13370 soil properties) with IES Ground contact set to None, so the U-value includes the ground. Thicknesses quoted exclude this layer.
Build-ups | Typical UK constructions sized to meet each value - not specific products.
Glazing | Windows, rooflights and glazed doors use whole-window U-values (glass + frame), as Part L defines them. g-values: 0.48 for non-domestic (the reference g-value in AD L Vol 2 Table 3.3, used for the solar gain check); 0.63 for dwellings (typical double low-e; Part L sets no g-value limit for dwellings - overheating is covered by Approved Document O).
DISCLAIMER
For modelling only. Meeting limiting U-values alone does not demonstrate Part L compliance. Part L 2026 applies from 24 March 2027 (24 September 2027 for higher-risk buildings), subject to transitional arrangements.

## 2026 Dwellings
BPEX | Building Performance Explained
Part L 2026 - Dwellings
Approved Document L Volume 1, 2026 edition ¦ BPEX_PartL_2026_Dwellings.py
Name in IES VE | What it is for | U-value W/m²K | Thermal mass κ kJ/m²K | g-value | Build-up, outside to inside | Source
Part L 2026_DWL_Roof Standard_0.16 | All roofs in new dwellings; improved (upgraded) existing roofs | 0.16 | 9 | – | Tiled pitched roof, loft insulation at ceiling level (425 mm) Clay roof tiles 12 / air gap 150 / Glass mineral wool loft roll 150.4 / Glass mineral wool loft roll between joists 100 / Plasterboard 12.5 mm | AD L Vol 1 (2026) Table 3.1 p.25; Table 3.3(b) p.28
Part L 2026_DWL_Roof Extension_0.15 | Roofs of extensions; new or replacement roofs on existing dwellings | 0.15 | 9 | – | Tiled pitched roof, loft insulation at ceiling level (442 mm) Clay roof tiles 12 / air gap 150 / Glass mineral wool loft roll 167.1 / Glass mineral wool loft roll between joists 100 / Plasterboard 12.5 mm | AD L Vol 1 (2026) Table 3.2 p.26
Part L 2026_DWL_Roof Existing Threshold_0.35 | Existing roof at the upgrade threshold | 0.35 | 9 | – | Tiled pitched roof, insulation between ceiling joists only (292 mm) Clay roof tiles 12 / air gap 150 / Glass mineral wool loft roll between joists 117.7 / Plasterboard 12.5 mm | AD L Vol 1 (2026) Table 3.3(a) p.28
Part L 2026_DWL_External Wall New_0.26 | Walls of new dwellings | 0.26 | 60 | – | Masonry cavity wall, full-fill mineral wool (312 mm) Brickwork 102.5 / Mineral wool cavity batt 96.6 / Aircrete block 100 / Lightweight gypsum plaster 13 mm | AD L Vol 1 (2026) Table 3.1 p.25
Part L 2026_DWL_External Wall Extension_0.18 | Walls of extensions; new or replacement walls on existing dwellings | 0.18 | 60 | – | Masonry cavity wall, full-fill mineral wool (367 mm) Brickwork 102.5 / Mineral wool cavity batt 151.3 / Aircrete block 100 / Lightweight gypsum plaster 13 mm | AD L Vol 1 (2026) Table 3.2 p.26
Part L 2026_DWL_External Wall Existing Improved Cavity_0.55 | Existing wall upgraded with cavity insulation | 0.55 | 191 | – | Brick/block cavity wall, blown mineral fibre cavity fill (277 mm) Brickwork 102.5 / Blown mineral fibre cavity fill 61.7 / Dense concrete block 100 / Dense gypsum plaster 13 mm | AD L Vol 1 (2026) Table 3.3(b) p.28
Part L 2026_DWL_External Wall Existing Improved Insulated_0.30 | Existing wall upgraded with internal or external insulation | 0.3 | 9 | – | Solid brick wall, internal insulation (PIR dry-lining) (302 mm) Brickwork 215 / air gap 15 / PIR foam board 60 / Plasterboard 12.5 mm | AD L Vol 1 (2026) Table 3.3(b) p.28
Part L 2026_DWL_External Wall Existing Threshold_0.70 | Existing wall at the upgrade threshold | 0.7 | 191 | – | Brick/block cavity wall, blown mineral fibre cavity fill (260 mm) Brickwork 102.5 / Blown mineral fibre cavity fill 44.5 / Dense concrete block 100 / Dense gypsum plaster 13 mm | AD L Vol 1 (2026) Table 3.3(a) p.28
Part L 2026_DWL_Floor Standard_0.18 | Floors of new dwellings and extensions; new or replacement floors | 0.18 | 215 | – | Ground-bearing concrete slab, PIR below slab (284 mm) PIR foam board 84.3 / Reinforced Concrete 150 / Sand-cement screed 50 mm on ground layer | AD L Vol 1 (2026) Tables 3.1 p.25 and 3.2 p.26
Part L 2026_DWL_Floor Existing Improved_0.25 | Existing floor upgraded | 0.25 | 16 | – | Suspended timber floor, mineral wool between joists (428 mm) air gap 300 / Mineral wool batt between joists 107.5 / Softwood 20 mm on ground layer | AD L Vol 1 (2026) Table 3.3(b) p.28
Part L 2026_DWL_Floor Existing Threshold_0.70 | Existing floor at the upgrade threshold | 0.7 | 215 | – | Uninsulated ground-bearing concrete slab (200 mm) Reinforced Concrete 150 / Sand-cement screed 50 mm on ground layer | AD L Vol 1 (2026) Table 3.3(a) p.28
Part L 2026_DWL_Party Wall_0.20 | Party walls in new dwellings | 0.2 | 60 | – | Masonry cavity party wall, full-fill mineral wool (344 mm) Lightweight gypsum plaster 13 / Aircrete block 100 / Mineral wool cavity batt 118 / Aircrete block 100 / Lightweight gypsum plaster 13 mm | AD L Vol 1 (2026) Table 3.1 p.25
Part L 2026_DWL_Door New_1.60 | Doors in new dwellings | 1.6 | 5 | – | Insulated door (effective core) (41 mm) Plywood sheathing 6 / Sectional door panel core (effective, incl. joints) 29.1 / Plywood sheathing 6 mm | AD L Vol 1 (2026) Table 3.1 p.25
Part L 2026_DWL_Door Extension_1.40 | Doors in extensions; replacement doors in existing dwellings | 1.4 | 5 | – | Insulated door (effective core) (48 mm) Plywood sheathing 6 / Sectional door panel core (effective, incl. joints) 36.2 / Plywood sheathing 6 mm | AD L Vol 1 (2026) Table 3.2 p.26
Part L 2026_DWL_Window New_1.60 | Windows, roof windows and curtain walling in new dwellings | 1.6 | – | 0.63 | Whole-window U-value (glass + frame). Double glazing, low-e outer pane, 16 mm gas gap, 4 mm clear inner pane; frame 30% of area (frame U 1.4) | AD L Vol 1 (2026) Table 3.1 p.25
Part L 2026_DWL_Window Extension_1.40 | Windows in extensions; new or replacement windows in existing dwellings | 1.4 | – | 0.63 | Whole-window U-value (glass + frame). Double glazing, low-e outer pane, 16 mm gas gap, 4 mm clear inner pane; frame 30% of area (frame U 1.4) | AD L Vol 1 (2026) Table 3.2 p.26
Part L 2026_DWL_Rooflight Standard_2.20 | Rooflights, new and existing dwellings | 2.2 | – | 0.63 | Whole-window U-value (glass + frame). Double glazing, low-e outer pane, 16 mm gas gap, 4 mm clear inner pane; frame 25% of area (frame U 2.0) | AD L Vol 1 (2026) Tables 3.1 p.25 and 3.2 p.26
Part L 2026_DWL_Glazed Door New_1.60 | Glazed doors in new dwellings | 1.6 | – | 0.63 | Whole-window U-value (glass + frame). Double glazing, low-e outer pane, 16 mm gas gap, 4 mm clear inner pane; frame 30% of area (frame U 1.4) | AD L Vol 1 (2026) Table 3.1 p.25
Part L 2026_DWL_Glazed Door Extension_1.40 | Glazed doors (>60% glazed) in extensions; replacement glazed doors | 1.4 | – | 0.63 | Whole-window U-value (glass + frame). Double glazing, low-e outer pane, 16 mm gas gap, 4 mm clear inner pane; frame 30% of area (frame U 1.4) | AD L Vol 1 (2026) Table 3.2 p.26
U-values are the limiting values the constructions are built to (calculated U-values are equal or slightly lower). κ calculated by BPEX from the layer build-ups. Glazing U-values and g-values are calibrated against IES VE's own calculation when the script runs.

## 2026 Non-domestic
BPEX | Building Performance Explained
Part L 2026 - Non-domestic buildings
Approved Document L Volume 2, 2026 edition ¦ BPEX_PartL_2026_NonDomestic.py
Name in IES VE | What it is for | U-value W/m²K | Thermal mass κ kJ/m²K | g-value | Build-up, outside to inside | Source
Part L 2026_NDOM_Roof Standard_0.18 | All roofs (pitched and flat): new buildings, extensions, replacement and improved roofs | 0.18 | 7 | – | Flat roof, PIR on profiled steel deck (123 mm) Single-ply membrane 2 / PIR foam board 118.9 / Profiled steel sheet 2 mm | AD L Vol 2 (2026) Table 3.1 p.26; Table 3.2(b) p.27
Part L 2026_NDOM_Roof Existing Threshold_0.35 | Existing roof at the upgrade threshold | 0.35 | 7 | – | Flat roof, PIR on profiled steel deck (64 mm) Single-ply membrane 2 / PIR foam board 59.6 / Profiled steel sheet 2 mm | AD L Vol 2 (2026) Table 3.2(a) p.27
Part L 2026_NDOM_External Wall Standard_0.26 | Walls of new buildings and extensions; new or replacement walls | 0.26 | 22 | – | Rainscreen cladding on steel frame (SFS), PIR sheathing (200 mm) Rainscreen 3 / air gap 50 / PIR foam board 72.5 / Cement bonded particle board 12 / air gap 50 / Plasterboard 12.5 mm | AD L Vol 2 (2026) Table 3.1 p.26
Part L 2026_NDOM_External Wall Existing Improved Cavity_0.55 | Existing wall upgraded with cavity insulation | 0.55 | 191 | – | Brick/block cavity wall, blown mineral fibre cavity fill (277 mm) Brickwork 102.5 / Blown mineral fibre cavity fill 61.7 / Dense concrete block 100 / Dense gypsum plaster 13 mm | AD L Vol 2 (2026) Table 3.2(b) p.27
Part L 2026_NDOM_External Wall Existing Improved Insulated_0.30 | Existing wall upgraded with internal or external insulation | 0.3 | 9 | – | Solid brick wall, internal insulation (PIR dry-lining) (302 mm) Brickwork 215 / air gap 15 / PIR foam board 60 / Plasterboard 12.5 mm | AD L Vol 2 (2026) Table 3.2(b) p.27
Part L 2026_NDOM_External Wall Existing Threshold_0.70 | Existing wall at the upgrade threshold | 0.7 | 191 | – | Brick/block cavity wall, blown mineral fibre cavity fill (260 mm) Brickwork 102.5 / Blown mineral fibre cavity fill 44.5 / Dense concrete block 100 / Dense gypsum plaster 13 mm | AD L Vol 2 (2026) Table 3.2(a) p.27
Part L 2026_NDOM_Floor Standard_0.18 | Floors of new buildings and extensions; new or replacement floors | 0.18 | 215 | – | Ground-bearing concrete slab, PIR below slab (284 mm) PIR foam board 84.3 / Reinforced Concrete 150 / Sand-cement screed 50 mm on ground layer | AD L Vol 2 (2026) Table 3.1 p.26
Part L 2026_NDOM_Floor Existing Improved_0.25 | Existing floor upgraded | 0.25 | 215 | – | Ground-bearing concrete slab, PIR below slab (250 mm) PIR foam board 50.1 / Reinforced Concrete 150 / Sand-cement screed 50 mm on ground layer | AD L Vol 2 (2026) Table 3.2(b) p.27
Part L 2026_NDOM_Floor Existing Threshold_0.70 | Existing floor at the upgrade threshold | 0.7 | 215 | – | Uninsulated ground-bearing concrete slab (200 mm) Reinforced Concrete 150 / Sand-cement screed 50 mm on ground layer | AD L Vol 2 (2026) Table 3.2(a) p.27
Part L 2026_NDOM_Pedestrian Door Standard_1.60 | Pedestrian doors, new and existing buildings | 1.6 | 5 | – | Insulated door (effective core) (41 mm) Plywood sheathing 6 / Sectional door panel core (effective, incl. joints) 29.1 / Plywood sheathing 6 mm | AD L Vol 2 (2026) Table 3.1 p.26
Part L 2026_NDOM_Vehicle Door Standard_1.30 | Vehicle access and similar large doors, new and existing buildings | 1.3 | 7 | – | Insulated sectional vehicle door (effective core) (52 mm) Profiled steel sheet 2 / Sectional door panel core (effective, incl. joints) 48 / Profiled steel sheet 2 mm | AD L Vol 2 (2026) Table 3.1 p.26
Part L 2026_NDOM_Window Standard_1.60 | Windows, roof windows and curtain walling, new and existing buildings | 1.6 | – | 0.48 | Whole-window U-value (glass + frame). Double glazing, solar control low-e outer pane, 16 mm gas gap, 4 mm clear inner pane; frame 10% of area (frame U 1.4) | AD L Vol 2 (2026) Table 3.1 p.26; g-value: Table 3.3 p.29
Part L 2026_NDOM_Rooflight Standard_2.20 | Rooflights, new and existing buildings | 2.2 | – | 0.48 | Whole-window U-value (glass + frame). Double glazing, solar control low-e outer pane, 16 mm gas gap, 4 mm clear inner pane; frame 25% of area (frame U 2.0) | AD L Vol 2 (2026) Table 3.1 p.26; g-value: Table 3.3 p.29
Part L 2026_NDOM_Glazed Door Standard_1.60 | Glazed pedestrian doors, new and existing buildings | 1.6 | – | 0.48 | Whole-window U-value (glass + frame). Double glazing, solar control low-e outer pane, 16 mm gas gap, 4 mm clear inner pane; frame 30% of area (frame U 1.4) | AD L Vol 2 (2026) Table 3.1 p.26
Part L 2026_NDOM_High-Usage Entrance Door Standard_3.00 | High-usage entrance doors (e.g. automatic or revolving), new and existing buildings | 3 | – | 0.48 | Whole-window U-value (glass + frame). Double glazing, solar control low-e outer pane, 16 mm gas gap, 4 mm clear inner pane; frame 30% of area (frame U 3.0) | AD L Vol 2 (2026) Table 3.1 p.26
U-values are the limiting values the constructions are built to (calculated U-values are equal or slightly lower). κ calculated by BPEX from the layer build-ups. Glazing U-values and g-values are calibrated against IES VE's own calculation when the script runs.

## Sources
BPEX | Building Performance Explained
Sources
Where the values come from
REGULATIONS
Document | Tables used | Applies to
Approved Document L, Volume 1: Dwellings, 2026 edition | Table 3.1 (p.25) new dwellings; Table 3.2 (p.26) new elements in existing dwellings; Table 3.3 (p.28) existing elements - threshold (a) and improved (b) | Dwellings script
Approved Document L, Volume 2: Buildings other than dwellings, 2026 edition | Table 3.1 (p.26) new or replacement elements in new and existing buildings; Table 3.2 (p.27) existing elements - threshold (a) and improved (b); Table 3.3 (p.29) reference glazing for solar gain (g 0.48) | Non-domestic script
CALCULATION METHODS
Standard / guide | Used for
BS EN ISO 6946 | U-values and surface resistances (walls 0.04 / 0.13, roofs 0.04 / 0.10, floors 0.04 / 0.17 m²K/W)
BS EN ISO 13786 | Thermal mass κ (simplified method, as IES VE)
BS EN ISO 13370 | Ground floors - equivalent ground layer
BS EN 410 | g-values (total solar energy transmittance)
SAP 10, Table 6b | Typical g-value of double low-e glazing (0.63) and frame factor 0.7 (30% frame) for dwellings
BR 443 (2006) | Conductivities, airspace resistances, timber fractions
CIBSE Guide A | Density and specific heat where BR 443 gives none
MATERIALS
Material | Source | λ ¦ ρ ¦ c | Name in IES VE
Aircrete block incl. mortar (equivalent) | 0.19 block + 6.7% mortar at 0.88 (BR 443 4.2) | 0.22 ¦ 600 ¦ 1000 | BPEX HL_ACB Aircrete block incl. mortar (equivalent)
Blown mineral fibre cavity fill | Typical 1980s declared value | 0.044 ¦ 30 ¦ 1030 | BPEX HL_MF44 Blown mineral fibre cavity fill
Brickwork, outer leaf (exposed) | BR 443 3.3 (outer leaf) | 0.77 ¦ 1700 ¦ 800 | BPEX HL_BRKO Brickwork, outer leaf (exposed)
Cement bonded particle board | IES system material (values as in IES) | 0.23 ¦ 1100 ¦ 1000 | BPEX STD_USP Cement bonded particle board
Clay roof tiles | CIBSE Guide A typical | 1 ¦ 2000 ¦ 800 | BPEX HL_TILE Clay roof tiles
Clear float glass 4 mm | Typical manufacturer values; optical properties calibrated in IES VE to the target g-value | 1.06 ¦ 2500 ¦ 840 | BPEX GL_CLR4 Clear float glass 4 mm
Dense concrete block | CIBSE Guide A typical, 2000 kg/m3 | 1.13 ¦ 2000 ¦ 1000 | BPEX HL_BLKD Dense concrete block
Dense gypsum plaster | CIBSE Guide A typical | 0.5 ¦ 1300 ¦ 1000 | BPEX HL_PLD Dense gypsum plaster
Glass mineral wool loft roll | Typical 2000s+ declared value | 0.04 ¦ 12 ¦ 1030 | BPEX HL_LW40 Glass mineral wool loft roll
Glass mineral wool loft roll between joists (9% joists, equivalent) | Area-weighted: 9.0% joists k 0.13 + Glass mineral wool loft roll k 0.04 (BR 443 4.5/4.6 fractions) | 0.0481 ¦ 55.9 ¦ 1488.7 | BPEX HL_E9LW40 Glass mineral wool loft roll between joists (9% joists, equivalent)
Ground, clay/silt (equivalent layer) | BS EN ISO 13370 Table 7 clay/silt: k 1.5, rho.c 3.0 MJ/m3K (RdSAP S5.5 soil) | 1.5 ¦ 1500 ¦ 2000 | BPEX HL_SOIL Ground, clay/silt (equivalent layer)
Lightweight gypsum plaster | CIBSE Guide A typical | 0.18 ¦ 600 ¦ 1000 | BPEX HL_PLL Lightweight gypsum plaster
Low-e glass 6 mm (soft coat, g approx. 0.63 in a double unit) | Typical manufacturer values; optical properties calibrated in IES VE to the target g-value | 1.06 ¦ 2500 ¦ 840 | BPEX GL_LOWE6 Low-e glass 6 mm (soft coat, g approx. 0.63 in a double unit)
Mineral wool batt between joists (11% joists, equivalent) | Area-weighted: 11.0% joists k 0.13 + Mineral wool batt k 0.037 (BR 443 4.5/4.6 fractions) | 0.04723 ¦ 81.7 ¦ 1413.7 | BPEX HL_E11MW37 Mineral wool batt between joists (11% joists, equivalent)
Mineral wool cavity batt (high performance) | Typical 2020s declared value | 0.032 ¦ 35 ¦ 1030 | BPEX HL_MW32 Mineral wool cavity batt (high performance)
PIR foam board | Typical 2000s+ declared value | 0.022 ¦ 32 ¦ 1400 | BPEX HL_PIR22 PIR foam board
Plasterboard | IES system material; k matches BR 443 3.6 | 0.21 ¦ 700 ¦ 1000 | BPEX STD_US1 Plasterboard
Plywood sheathing | BR 443 3.7 / 4.5 | 0.13 ¦ 500 ¦ 1600 | BPEX HL_PLY Plywood sheathing
Profiled steel sheet (modelled 2 mm) | Steel 50 W/mK; real sheet 0.5-0.7 mm, modelled 2 mm to avoid IES thin-layer instability | 50 ¦ 7800 ¦ 450 | BPEX HL_STL Profiled steel sheet (modelled 2 mm)
Rainscreen | IES system material (values as in IES) | 50 ¦ 7800 ¦ 450 | BPEX STD_SM1 Rainscreen
Reinforced Concrete | IES system material; k matches BR 443 3.4 | 2.3 ¦ 2300 ¦ 1000 | BPEX STD_CC2 Reinforced Concrete
Sand-cement screed | BR 443 3.4 (screed) | 1.15 ¦ 2000 ¦ 1000 | BPEX HL_SCR Sand-cement screed
Sectional door panel core (effective, incl. joints) | Effective conductivity so a 40 mm panel matches the whole-door U-value | 0.08 ¦ 40 ¦ 1400 | BPEX HL_DCORE Sectional door panel core (effective, incl. joints)
Single-ply membrane (modelled 2 mm) | PVC membrane typical | 0.16 ¦ 1400 ¦ 1000 | BPEX HL_SPM Single-ply membrane (modelled 2 mm)
Softwood | BR 443 3.7 | 0.13 ¦ 500 ¦ 1600 | BPEX HL_SWD Softwood
Solar control low-e glass 6 mm (g approx. 0.48 in a double unit) | Typical manufacturer values; optical properties calibrated in IES VE to the target g-value | 1.06 ¦ 2500 ¦ 840 | BPEX GL_SOLAR6 Solar control low-e glass 6 mm (g approx. 0.48 in a double unit)
λ = conductivity W/(m·K), ρ = density kg/m³, c = specific heat J/(kg·K)